## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Pembroke Court
Hylton Lane
Downhill
SR5 4DF
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-13735
DATE OF REPORT: 23/12/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-13735
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Pembroke Court
Hylton Lane
Downhill
SR5 4DF
Carried Out On | 21/12/2021, 23/12/2021
Survey Completed By | Kieran Holmes
SECTION 2: Introduction
No heating in communal area- Boiler located next to flat 41 and shows a gas bottle icon ---- ---- Standard Callout for Commerical Boilers

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-13735
SECTION 3: Report
Electrode assembly kit needed ASAP Potterton promax 28 erp GC 47-393-48 Had to turn boiler off Burner seal had deteriorated on boiler causing damage to wiring in burner chamber. Changed electrode assembly kit as above Also changed ignition wiring harness 5114783 Fan wiring harness 5114777 Ignition lead to spark electrode 5114701 Ionisation lead 5114749 Combustion gasket 5114755 After all these parts were changed when I tried to run boiler I was going a E130 and E131 fault pointing to an issue with NTC sensor ontop of main heat exchanger which could have been damaged from the failed burner gasket. This needs changing as was only getting 5ohms when testing and should have been 20. Part number for NTC sensor is 5114747. I have ordered into consett for collection 24/12/21. If it doesn't get delivered I have also reserved one at team Valley parts centre. This sensor sits in a dry pocket ontop of heat exchanger so will ot take long to change. Once changed the boiler will need FGA readings taken as was unable to take them today due to boiler going to fault. KH 23/12/2021.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-13735
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-13735
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-13735
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-13735
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-13735
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes