## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
22 Lynwood House
Durham Road
Lanchester
DH7 0LS
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-5972
DATE OF REPORT: 28/01/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-5972
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | 22 Lynwood House
Durham Road
Lanchester
DH7 0LS
Carried Out On | 04/01/2021, 26/01/2021, 28/01/2021
Survey Completed By | Craig Nicholson
SECTION 2: Introduction
3 x zones not heating removed actuator heads to give heat. now tenant cannot turn heating down

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-5972
SECTION 3: Report
Attend site 1545 for heating issues Gain access to heating controls/manifold, re fit actuator heads to manifold . open up the flow restricters to allow more flow and test operation of all components ( room stats, actuator's time clock)all working ok, Flow temp now at 45° and return temp 27° and heating slabs warming up Offsite 1630 complete Attended site 26/1/21 Once gaining access to manifold/controls to check temperatures, which where 44degrees flow and return temperature 32degree’s. As the issue’s where located on the same area/ wing, I.e. flat numbers 20-22, i gained access to the plant room, to find out of a bank of two main CHB’s only one was operational. Due to safety failure when annual service was carried out, only allowing system 50% operational. Once second CHB repair is carried out, system will achieve the optimal temperatures required and demanded. Attended site 28/1/21 Once gaining access to manifold/controls to check temperatures, which where 44degrees flow and return temperature 32degree’s and correct operation identified As the issue’s where located on the same area/ wing, I.e. flat numbers 20-22, i gained access to the plant room, to find out of a bank of two main CHB’s only one was operational. Due to safety failure when annual service was carried out, only allowing system 50% operational. Once second CHB repair is carried out, system will achieve the optimal temperatures required and demanded. Also found that heating circulator no 1 in plant room with a bearing fault, which also failed to auto change to no 2, also found that a 46-48degree set point to BMS, which would be required to be increased due to the outside air temperature’s. So that 40% of the tenants would feel the comfort, without having to have the UFH on continually for near 24hr period, without any temperature increase. Further investigations/works required BMS/Controls engineer to attend to adjust set point, also to investigate failure on pump change over. Heating pump no1 to be replaced/ rewound. CHB no1 to be fully stripped and repaired as per L.C. Advisory’s.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-5972
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-5972
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-5972
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-5972
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-5972
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes