## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Room B Mowbray House
Rawdon Road
Sunderland
SR5 5PN
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-6200
DATE OF REPORT: 04/02/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6200
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Room B Mowbray House
Rawdon Road
Sunderland
SR5 5PN
Carried Out On | 21/01/2021, 22/01/2021, 27/01/2021, 01/02/2021, , 02/02/2021, 03/02/2021
Survey Completed By | Craig Nicholson
SECTION 2: Introduction
Boiler dripping from bottom. Contained with dish. Heating still on. No covid issues. Boiler in the communal kitchen.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6200
SECTION 3: Report
Attended site to investigate leaking boiler. Found when removing front cover, found the flow switch cracked, due to the leak running down toward major electrical cables, and components the CHB has been drained and isolated electrical and gas. Ordered new flow switch for wolesley Sunderland, Dave Aston has requested i return 22/1/21 as first appointment, to carry out remedial works, to re-instate the CH/DHW. Please not that immersion has been turned on so that site have the ability of DHW. 22/1/21 Attended to fit new flow switch to the appliance. Carried out replacement, checked all connections found all good, when filling up system. When attempting to run up the CH/DHW system, boiler had begun to lockout on dry fire. After further investigations I found the system severely air locked, and due to failed AAV’s, also the system pipe work it was failing to circulate around the cylinder coil. I disconnected the new flow switch to allow the boiler to ignite, after several hours, of venting via the pump vent screw and pulling the air lock out with a wet vacuum, full operation was achieved. Note: system condition I.e. water content and pipe work configuration is very poor. And radiators showing signs of oxidisation build up. Boiler approx age 16 years old. Recommend when season changes, that a complete system upgrade/replacement carried out. C.N 27/1/21 11:45-14:30 Attended site for low ch temperatures. When on site found system still struggling to circulate, which is causing to reach temperature quicker than normal. Have reduced boiler temperature to increase boiler operation for longer periods so that the building has heating, even at at reduced operating capacity of 40-50%. Further investigations As previously reported, when on site at Alexander house, i identified a secondary leak on the elson manifold, after speaking with David Hunter, he instructed me to carry out repair to failed manifold pipe work section. Preventing any damage to property. 5x heaters have also been delivered to site, as back up measure across both properties. Will return ASAP to carry out remedial works to manifold as per instructions. Further works. Would recommend full system flush, boiler and system upgrade to unvented heating systems (system boilers) across both Alexander/Mowbray house. As current boiler and controls are approx 16 years old. Current heating circuit open vented, signs of corrosion to 60% of the radiators on both sites. Attended 2/2/21 Once manifold had been removed and all pipe work re-connected to system, linked out flow switch to prevent dry fire fault, to allow boiler ignition and for the heat to circulate. After several hours at attempting to remove air lock, I had been instructed to replace existing pump as it was fairly old, to push flow around the primary circuit. Once fitted I found a slight improvement in removing the air within the system. I later found two failed capillary joints to the flow and returns in the ceiling space, once drained I cut out a section of the ceiling exposing both of the failed fittings. I then carried out the pipe work replacement, then filled and checked for any leaks. When the system was full I began to attempt to remove the air in the primary circuit, after a further several hours also after speaking with David Hunter, he instructed me to attend with him on the first job 3/2/21 to assist In regards to rectifying this issue. Attended 3/2/21. 07:40-14:00 Re-piped up primary and secondary heating returns as per instruction, once completed I filled system checking for leaks none found. I then begun to removed the air in the primary circuit, achieving optimal temperatures across the flow and return. Once the coil had correct circulation, i then turned on the heating circuit, allowed radiators within the site to slowly gain temperature. System fully operational, and correct functionality achieved.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6200
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6200
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6200
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6200
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6200
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes