## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
15 Lynwood House
Durham Road
Lanchester
DH7 0LS
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-6257
DATE OF REPORT: 28/01/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6257
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | 15 Lynwood House
Durham Road
Lanchester
DH7 0LS
Carried Out On | 26/01/2021, 28/01/2021
Survey Completed By | Craig Nicholson
SECTION 2: Introduction
Tenant advised that the underfloor heating isnt keeping her warm she advised, someone attended at the beginning of the month and advised they had turned the heating up but tenant advised its not heating correctly and shes struggling to keep warm.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6257
SECTION 3: Report
Attended site to investigate low UFH. Have increased flow rate to manifold, to 3/Lpm in doing so I’ve achieved a 4 degree increase on both the flow and return manifolds, and a slow increase. Have advised customer that due to slow uptake and temperature increase, to monitor and report if no temperature increase is achieved throughout the evening and the coming days. If required to carry out further investigations to why the the UFH isn’t achieving the correct flow and return temperatures. Attended site 28/1/21. Found when gaining access to the plant room that heating pump no1, showing bearing fault. With BMS failing to change over duty to pump 2, also that CH/UFH heating set point only set 46-48. Due to this issue it’s creating a flow reduction across the building, also CHB no1 isolated reducing heating functionality to 50%. Manifold fully functional, main plant room issue.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6257
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6257
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6257
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6257
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6257
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes