## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
34 Mayfield Park
Bristol Drive
Wallsend
NE28 9RH
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-6266
DATE OF REPORT: 26/01/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6266
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | 34 Mayfield Park
Bristol Drive
Wallsend
NE28 9RH
Carried Out On | 26/01/2021
Survey Completed By | Craig Nicholson
SECTION 2: Introduction
Call Details No Heating on again. Please treat as Urgent.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6266
SECTION 3: Report
Attended site for low temperatures from UFH. Found on UFH flow temperature of 40 degrees and return temperature of 32 degrees. With lounge and bathroom room thermostats calling for heat. When gaining access to the plant room, flow temperatures on zone 1, only where sitting at 43-46 degrees, which weren’t ideal and reduced temperatures to the opposite side of the building, after adjusting pump settings to constant curve, and also cleaning out both inline strainers for both zone 1-2, I observed temperature increase via the BMS (see pictures attached). Then I returned to no 34, and observed a 10degree increase on both the UFH flow and return respectively. With a digital laser thermostat I recorded floor temperatures, lounge, and kitchen. Have emailed all pictures and findings to admin email.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6266
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6266
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6266
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6266
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6266
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes