## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Burn Promendade
Burn Park Road
Houghton-Le-Spring
DH4 5EJ
CARRIED OUT ON BEHALF OF
Castles & Coasts Housing Association
REPORT NUMBER: 21-6268
DATE OF REPORT: 04/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6268
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Castles & Coasts Housing Association
Address | Arcadia House
Balliol Business Park
Newcastle Upon Tyne
NE12 8EW
Site Address | Burn Promendade
Burn Park Road
Houghton-Le-Spring
DH4 5EJ
Carried Out On | 04/03/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
Water temperature monitoring identifed that hot flow and retuen temperatures are lower than required for sentinal outlets. this appears to have been ongoing since October 2020 please investigated and make necessary adjustments - Commercial Boiler

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6268
SECTION 3: Report
Attend site 1345 Attend site to investigate Dhw temperature issues Find no automatic control for the primary circuit to the calorfiers and no electronic monitoring of the dhw temp. The only control is 2 no manual adjusted 3 way valves these need actuators fitted and linked into the bms so it can automatically regulate the dhw temp. Also find theres a Horn mixing valve directly fitted on the hot feed from the calorfiers this mixes the dwh temperature down to 50° going into the building this is set to its highest and no further adjustment avaliable The bms work and actuator install will need a controls engineer to carry this out. Offs1545 complete

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6268
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6268
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6268
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6268
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6268
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes