## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Rosebank Hall
Willington Terrace
wallsend
NE28 7BT
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-6407
DATE OF REPORT: 08/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6407
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Rosebank Hall
Willington Terrace
wallsend
NE28 7BT
Carried Out On | 09/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Replacement of internal flue on boiler plant.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6407
SECTION 3: Report
LPC 9.2.21 0810 - 1030 TEMP FIX ONLY Called to suppliers and collected parts as req , then proceeded to job . Arrived on site and gained access to plantroom area . Removed damaged internal flue from boiler no.2 middle , fitted new sump gasket and new inner flue as req . Reconnected 28 mm gas supply as left capped off . Attempted to sort out damaged internal plastics , as badly damaged due to long exposure to condensate . Fired up and tested for safe operation in both high and low fire modes as req . When I went to fit front casing , found that plastic box hinges that houses electrics to be damaged . This forms a seal when the front casing is fitted , this is a room sealed boiler . Carried out emergency temporary repair and applied heat proof silicone to front boiler casing, around user interface to create a seal . The internals of the boiler can be accessed, just req the thin bead of silicone cutting away ( ONLY A TEMP FIX ) Due to the long exposure to condensate and products of combustion and the damage caused to various components ( electrics , gas valve solenoids , internals plastics, wiring harness , a new boiler is req to be installed. A co detector has been installed as a safe measure. Warning notice issued as appliance is AT RISK , due to condensate damage . Appliance details Boiler 2 middle Remeha Quinta pro 115 115 keep, not rated Sn , 1113702350700 GFA High fire 02 , 4.8 Co2 , 9.1 Co , 36 ppm Ratio , 0.0003 Low fire 02 , 6.1 Co2 , 8.4 Co , 5 ppm Ratio , 0.0000

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6407
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6407
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6407
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6407
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6407
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes