## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Spring View
Bristol Drive
Battle Hill
NE28 9TH
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-6411
DATE OF REPORT: 10/02/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6411
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Unit 1 Hunslet Trading Estate
Servern Way
Hunslet
Leeds
LS10 1BL
Site Address | Spring View
Bristol Drive
Battle Hill
NE28 9TH
Carried Out On | 10/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Heating not working properly The Tenant has said she is cold. Please attend 10.02.21. Flats 25, 17 & 18

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6411
SECTION 3: Report
LPC 10.2.21 1035 - 1320 Arrived on site and gained access to plantroom area. Found the 3 x Hamworthy Fleet 50 modules, to be in fire but only generating 52 c of water . Checked working pressure at gas meter , found to be ok . Tested working pressure within the plantroom , with all appliances in fire fire , again ok. U40 Gas meter fitted- roughly will supply 400 kw Carried out GFA in each module in both high and low fire modes , found modules to be running low . Adjusted in high and low fire until 9.0 % co2 achieved , found allothet readings to be well within manufacturers specifications. Monitored functions and performance of all modules , turned speeds down on each individual shunt pumps , in hope to allow and gain better heat transfer . Found CH flow temp to building now risen from 50c to roughly 57 c , and modules now generating more heat . Reqs monitoring daily .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6411
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6411
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6411
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6411
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6411
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes