## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
The Manors (Boiler Works)
Adderlane Road
West Wylam
NE42 5ET
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-6453
DATE OF REPORT: 30/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6453
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | The Manors (Boiler Works)
Adderlane Road
West Wylam
NE42 5ET
Carried Out On | 12/02/2021, 30/03/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
Ongoing boiler works DH/LC DA - Repairs. New cert to be produced.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6453
SECTION 3: Report
LPC 12.2.21 0830 - 1140 Attended site and carried out emergency works on boiler no.1 , as only boiler now running. Carried out a series of tests on components and found that fan has failed . Removed fan assembly from boiler no.2 , that is not in as gas supply capped off , due to leak on gas valve. Fitted fan to boiler no.1 and tested for leaks across gas valve , all ok . Fired up and tested operation of fan in both high and low speeds , found to be very noisy applied lubricant and ran smoothly . Carried out GFA to ensure safe operation in both hoghband low fire modes. Tested all saftey features on appliance, found to be ok . Monitored functions and performance, to ensure against failure of components. Cannot guantee how long fan will last , as removed from a similar aged appliance . The AT RISK warning notices still stand issued earlier this week , due to flue joint not able to inspect and all internal and front casing plastics damaged by condensate exposure . Allowed time for the DHW storage to recover and now at 65 c , pulled DHW through taps to building and checked temps at kitchen taps all ok . All parts req orderd with Steve at Silver link Parts Centre as req. GFA ( boiler 1 LHS ) High fire 02 , 5.4 Co2 , 8.8 Co , 44 ppm Ratio , 0.0005 Low fire 02 , 4.3 Co2 , 9.4 Co , 16 ppm Ratio , 0.0002 Attend site 30/03/21 0900 picked up parts 0730 -0900 Gain access to plant room and replace all the bits on the boi,er no 2 which were faulty 1 no gas valve 1 no fan assembly 1 no gas train and replace all gaskets parts all from feetham Court the boiler which was taken out earlier this year Commission and test All boilers now working Off site 1315 complete

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6453
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6453
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6453
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6453
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6453
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes