## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
1-31 Chapelville
Front Street
Seaton Burn
NE13 6EH
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-6456
DATE OF REPORT: 12/02/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6456
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | 1-31 Chapelville
Front Street
Seaton Burn
NE13 6EH
Carried Out On | 12/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
The hot water boiler in plant room tripped - please investigate.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6456
SECTION 3: Report
LPC 12.2.21 1250 - 1410 Attended site and gained access to the plantroom , water heater no.2 no running. Found that pump in appliance is causing the breaker to trip within the control panel. There is a very strong smell of burning present at the internal pump. This is the same as what happened to water no.1 a few ago . Isolated the appliance from the DHW circuit to prevent , cooling the water temps and made safe . Water heater no.1 is running with no issues at the moment. The flow and return sensors have already been orderd with Spencer at border heating, this was done before the pump had failed . I cannot guantee that further works and components will not be req , as unable to currently test appliance . Tested DHW temps in the building all found to be ok . Lochinvar SHW60 - 325CE Sn , K14C20074551 See image attached of data badge Parts req Inlet / return thermister Outlet / flow thermister Flue sensor Internal pump

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6456
SECTION 4: Photos
Room / Area
Plantroom
Description
Lochinvar water heater no.2 data badge
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6456
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6456
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6456
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6456
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes