## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
3 Filey Road
Scarborough
Yorkshire
YO11 2SF
CARRIED OUT ON BEHALF OF
HG Morgan Sindall
REPORT NUMBER: 21-6589
DATE OF REPORT: 24/05/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6589
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | HG Morgan Sindall
Address | Sheffield South
Yorkshire
S9 2UB
Site Address | 3 Filey Road
Scarborough
Yorkshire
YO11 2SF
Carried Out On | 21/02/2021
Survey Completed By | Darren Reay
SECTION 2: Introduction
Air Source heating system not working

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6589
SECTION 3: Report
Attended site to report of heat pump failure, No heating or DHW. Heat pump was found to be in a fault state (E3) high pressure fault. The client reported being without heating or hot water for some 9 days. Filters stripped out to investigate possible obstruction, none found as had been serviced some 2 months ago. Attempted to put the heat pump into operation but the fault would not clear. Hard reset the heat pump and carried out factory reset then put the unit into operation. Faulted for a second time with E3 fault. Noticed the ESBE valve had not fully acuate and was slow to respond , isolated pipework and stripped out ESBE to asses, no restriction found. Manually actuated the valve to free up. Hard reset the unit and put into operation. The client mentioned the immersion heater was also not working. Accessed the loft and found the thermal trip had pulled out. Re-set and tested. System all up and running and left operating. The compressor was noticeably loud on start up, suspect imbalanced scroll or lack of oil. The system was monitored while it achieved the cylinder recharge and into heating. The compressor did quiet down after running for a period of time.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6589
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6589
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6589
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6589
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6589
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes