## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Chapelville
Front Street
Seaton Burn
NE13 6EH
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-6630
DATE OF REPORT: 24/02/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6630
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Chapelville
Front Street
Seaton Burn
NE13 6EH
Carried Out On | 24/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Various are complaining about having no hot water. Please remedy and treat as urgent.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6630
SECTION 3: Report
LPC 24.2.21 1155 - 1610 Arrived on site and gained access to building , spoke to site manager ( Jackie ) who informed me of the issues on site . Checked DHW water heater , pumps etc and found to all be ok . Jackie then supplied me a detailed list of all rooms that have reduced DHW temps . Went around every flat on this section of the building , and tested mixer taps and showers. Found that short mixer valves have failed in flats 5 and 11 , causing massive issues . I then shut off the hot water supplies to these flats , and retested the flats . Found all flats now to have normal DHW temps restored , proving that flats 5 & 11 are the issue. Also flat no 4 reqs a new WHB mixer tap as it has terrible water hammer , that can be heard and felt through the entire area . Info supplied to David Hunter to pass on to Morgan Sindall to carry out works .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6630
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6630
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6630
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6630
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6630
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes