## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Carisbrooke Court
Chester Terrace
Sunderland
SR1 3SN
CARRIED OUT ON BEHALF OF
Castles & Coasts Housing Association
REPORT NUMBER: 21-6657
DATE OF REPORT: 19/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6657
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Castles & Coasts Housing Association
Address | Arcadia House
Balliol Business Park
Newcastle Upon Tyne
NE12 8EW
Site Address | Carisbrooke Court
Chester Terrace
Sunderland
SR1 3SN
Carried Out On | 14/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Annual Gas safety Checks. Service - TCH - CCHAGS052021 Karbon Gas Service May 2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6657
SECTION 3: Report
LPC 14.4.21 0820- 1630 Attended site and carried out commercial gas tightness test as per the guidance published in UP1A. The gas meter is located in a rear outbuilding, right behind the plantroom . There is a large wooden louverd door that provides ventilation to the area , there is a lock present and the key is identified. The gas transporters warning advice label is present and completed. Both the ECV and AECV are smooth operating , the AECV does not fall to the closed position and has been fitted upside down . The ECV has a label of operation attached to it , earth bonding is also present at the meter . The gas pipe work with the meter room is showing signs of corrosion ( as untreated) The gas pipe work from the meter to the plantroom , is sleeved though the wall ( again corroded ) The pipe work then tees off and runs through the building , via a suspended ceiling ( not sleeved through wall ) Pipe work is not identified and finally terminates at the fire place, where its reduced down to 10 mm copper with a compression cap. Pipe work is running through an unventilated boxing / duct , and non gas families ecv used . With in the plantroom gas pipe work is identified along its route, and well supported. The 2 x boilers have gas ECVS fitted , whilst the 2 x water heaters have own manufacturers gas taps . Test and purge points are not fitted , no emergency stop button fitted etc . Traced gas pipe work along its entire route , calculated the total volume . Warning notice has been issued for corrosion to pipe work , pipe work ran in an unventilated duct , non gas families ECV fitted ,not sleeved through wall and pipework not identified. IVP - 0.0685 m3 IVF - 0.00685 m3 IMV - 0.067 m3 total - 0.14235 m3 S.O.S - the lounge area > 60 m3 MAPD - 4.2 mb Letby - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result.... Pass , zero drop recorded or detected with appliances connected. Whilst on site I carried out an annual gas saftey inspection , on 2 x boilers and 2 water heaters . The 2 x water heaters are atmospheric natural draught , on a flue dilution system . The 2 x boilers are open flue B23 on a shared flue . The general quality of the entire install is extremely poor . Water heaters . The flue dilution system is fully interlocked , so when the fan motor is turned the appliance shuts down. The condition of the flue is really bad as temporary repairs have been carried out to the flexible connections , either side of the fan motor . These are have taped over and ate leaking at the products of combustion at the moment . The flue itself is dilapidated and also held together with tape . The system does not have dampers fitted either on each flue from the individual appliances , or on the air intake side. This could easily be creating flame lift due to the velocity the fan is extracting the products of combustion, through the heat exchangers . The elbow from the appliances have been cut down , and are barely overlapping the appliance connector . The gas valve adjustment screw in water heater 2 RHS , is damaged and burner pressure cannot be adjusted. The current burner pressure setting is 9.3 mb , when it should be 10mb . The other water heater has the burner pressure adjustment cap missing , I have applied foul tape over it . The 2 x free standing heating boiler are Potterton sirius FS70 's. The flue sample point cap is completely Seized into its housing .This is the only way of carrying out GFA on the appliance , without physically drilling the flue . The sample point is part of the appliance and will req replacing . The flue from the 2 x boilers has signs of corrosion present , but is not currently leaking ( as looks like leaks have been repaired ) Both individual flues are suspended from the ceiling, then they leave the plantroom via holes in the ceiling. The flues do not have fire stops fitted to then , the then run vertically through the building. I have gained access to the guest bed room above , found that the flues are running via a brick built chimney. I do not know if the liner has been used or not . Combustion and cooling ventilation is supplied via a wooden Louvred door, with vents at low , mid and high levels . The door communicates directly to outside . I have measured and calculated the total ventilation supplied , and at low level it is more than the 10 % allowance undersized. However the high level does supply more than req and makes up the shortfall , but the ventilation supplied is not in the correct configeration/ definition. The plantroom door req a large grill cutting into the lower half of the door . Ventilation req at low level - 1362 cm2 Actual ventilation in place - 902.4 cm2 ventilatio at high level- 681 cm2 Actual ventilation at high level - 1610 cm2 Appliance details Water heater 1 RHS Andrews 65/173PP Sn , GH13834408 50 kw , not rated Burner pressure - 10 mb GFA 02 , 6.0 Co2 , 8.4 Co , 0 ppm Ratio , 0.0000 Water heater 2 LHS Andrews 65/173PP Sn , DJ9602927 50 kw , not rated Burner pressure - 9.3 mb - due to damaged screw on gas valve , but operating safely- new gas valve req . GFA 02 , 9.2 CO2 , 6.6 CO , 0 PPM Ratio , 0.0000 Paper Warning notice issued as AT RISK , water heaters left isolated via gas valve . Gas cert suspended until works carried out . See Dave Aston for report

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6657
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6657
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6657
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6657
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6657
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes