## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Holmewood House
13 Esplanade West
Sunderland
SR2 7BG
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-6745
DATE OF REPORT: 02/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6745
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Holmewood House
13 Esplanade West
Sunderland
SR2 7BG
Carried Out On | 02/03/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
No heating/hot water ---- Flats 9 and 10-reported by Linda Staff

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6745
SECTION 3: Report
LPC 2.3.21 1450 - 1630 Arrived on site and gained access to main building area , parked at rear of building in large carpark . I was taken up the kitchen area where a Potterton Promax Combi is installed . Foynd that boiler has lost all of its pressure , used filling loop and topped up to correct pressure . This boiler supplies CH to Flats 9 & 10 with radiators in the kitchen , hallway and the bathroom areas . I have not been allowed access in the actual flats that have reported heating issues . I am only allowed access to the core areas , so unable to physically test the individual radiators in the flats . Found the isolation valve in the return to the boiler, to be turned fully off . Turned valve back on and created a demand and fired up appliance , monitord functions and performance. Found that the temperature was ramping up to high temperature, very fast above normal modulation levels . Attempted to remove magna clean from pipe work , as may be causing a restriction due to sedement/ sludge at . Unable to remove top of filter new magma clean unit has been orderd. Checked that boiler has a bypass fitted , the bathroom rad is the bypass rad and both valves open . Also expansion is full of water and will req replacing. Would also reccommed replacing DHW and CH thermisters . As this is an ERP model it's quite possible that the must have be damaged, with the return turned off and attempted to be used . All items orderd items orderd with Spencer at border heating.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6745
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6745
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6745
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6745
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6745
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes