## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Weavers Court
Swordy Drive
Alnwick
NE66 1SZ
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-6768
DATE OF REPORT: 04/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6768
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Weavers Court
Swordy Drive
Alnwick
NE66 1SZ
Carried Out On | 04/03/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Catering Gas Check - as per DH

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6768
SECTION 3: Report
LPC 4.3.21 1215 - 1630 Attended site and carried out commercial catering saftey inspection , as per guidence published in UP19. The gas catering equipment consists of 1 x high level grill , 1 x open top range and 1 x fryer , all in fair condition . Every FSD and thermostat has been tested individually, to ensure safe operation . The data badge on the Falcon grill is worn away and is unreadable , I have checked and found that the burner pressure on all Falcon grills is 15 mb. I do not know the exact model or the kw , but I can only prove that the appliance is operating safely. Each appliance has the correct catering hose and restraint fitted , where necessary and they are fitted correctly ( not touching the floor and bayonet fittings in correct orientation ) The steel pipe work manifold is fully identified and well supported along its route. Purge and test points are present, each appliance has it's own ECV fitted . The kitchen has it's own secondary U16 gas meter , located externally in a purpose built meter housing . There is a ECV fitted before the meter , that is difficult to operate as very close to inside of meter housing . The pipe work then enters the kitchen area a low level, with a ECV for localised isolation purposes. I cannot see if the pipe work is sleeved through the wall or not . I have carried out a localised tightness test from the U16 meter , found pupw work to be gas tight as now drop with appliances connected . The kitchen has mechanical ventilation fitted that is delivered to area via grills in the ceiling. The ventilation is interlocked to the gas supply , If ventilation is turned off , the gas supply is isolated to the area. There is a canopy installed that has the correct overhang, with baffle filtration . The canopy is interlocked to the gas supply , if the extract is turned off the gas supply is isolated to the area. The interlock panel is an S & S CT1200S , that monitors both extract and ventilation . Panel is manual reset with a key and no way of bypassing functions . The panel has a stop button built in , when pressed the gas supply is isolated . There is also another stop button at the entrance / exit door , again when pressed the gas supply is isolated to the area . The gas solenoid that is interlocked is located in the steel manifold behing the electric combi oven . The speed controllers for the extract and ventilation, are located to the RHS of the canopy . Carried out ambient co/co2 test as per UP19 , closed all windows and doors . Lit all burners and turned to maximum to create full load . Mechanical extract and ventilation at minimum speeds , left running for 20 minutes. Tested at middle of kitchen at two metres high , at the skirt of the canopy , and finally in front of the appliances. Found readings to be well below permissible limits . Appliance details Grill Falcon Model and serial number etc , not known as data badge unreadable . Burner pressure - 15 mb Range Falcon G3101 Sn , F571263 38.9 kw , not rated Burner pressure - 15 mb Fryer Pitco 35C+ Sn , G16BB005280 26 kw , not rated Burner pressure - 10.8 mb.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6768
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6768
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6768
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6768
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6768
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes