## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
5 Old Customs House
65-67 Borough Road
North Sheilds
NE29 6LH
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-6772
DATE OF REPORT: 08/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6772
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | 5 Old Customs House
65-67 Borough Road
North Sheilds
NE29 6LH
Carried Out On | 04/03/2021, 07/04/2021, 08/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Tenant at flat 5 reports ongoing issues with heating after callout on Monday. His radiators are not working. He is unsure if others in the property are having similar issues. No covid concerns but vulnerable customers tenant on flat 5 has underlying health conditions.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6772
SECTION 3: Report
LPC 7.4.21 0930 - 1055 Arrived on site and gained access to plantroom , at rear of property . Found that boiler no.3 RHS is not running , as attended originally on a callout . Carried out a series of tests , to identify the reason for the failiure . Found that the hot surface ignitor has failed , checked that LMU is supplying power to component- ok Attempted to locate a new ignitor , but non instock with our usual suppliers . I have orderd 2 x new hot surface ignitors from Spencer at border heating , 1 x to repair boiler 3 and 1 x for site stock . Due in tomorrow as orderd for next day delivery ( 8.4.21) LPC 8.4.21 Call to suppliers to collect parts , as just arrived via overnight courier service . Proceeded to site address , arrived at job and gained access to plantroom area. Fitted new style hot surface ignitor to boiler no.3 RHS as req. Fired up and tested functions and performance, monitored through modulation stages as making a loud fluting noise. Carried out GFA and found readings to be well out as largely undergased , causing reverberations. Set up in both high and low fire modes , until correct and acceptable GFA reading . Finally got appliance running correctly , I would highly recommend removing the burners and carrying out a full invasive service ( Gaskets etc will req ) Appliance details Boiler 3 RHS Hamworthy Variheat 110 GFA High fire 02 , 4.6 Co2 , 9.2 Co , 13 ppm Ratio , 0.0001 Low fire 02 , 4.2 Co2 , 9.5 Co , 54 ppm Ratio, 0.0006

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6772
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6772
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6772
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6772
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6772
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes