## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Aldwych House
Commercial Road
South Sheilds
NE33 1UE
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-6840
DATE OF REPORT: 15/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6840
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Aldwych House
Commercial Road
South Sheilds
NE33 1UE
Carried Out On | 08/03/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Follow up works from service - Parts to be invoied on this number

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6840
SECTION 3: Report
0820 - 1615 Called to suppliers and collected new damper drive actuators , then proceeded to site . Arrived on site but unable to gain to plantroom as keys missing . Eventually gained access once Liz the site manager , located keys . Fitted new low fire flue damper actuator to boiler no.1 , wired up as req . When I was originally on site this appliance was not running, so could not be tested at that time . Fired up and set burner pressure on both low and high fire modes , tested for spillage . Allowed time for flue to fully heat and then carried GFA. Found readings to be ok on low fire, but on high fire producing dangerous levels of co. This issue has been present for a while as the gas valve had been adjusted to 8 mb instead of the correvt 11 mb to achieve decent readings prior to my attendance. Foynd boiler no.1 to be IMMEDIATELY DANGEROUS and gas supply capped off and made safe . I suspect that there is an issue with the heat ex changer , but to fully access this to carry out a detailed inspection , the flue will req removing . Carried out the same works to boiler no.2 , but found this to be running all ok with no issues . Achieved good GFA readings both high and low fire , burner pressures correct . Monitored functions and performance all ok , 3 x out of the 4 x boilers now running . Boiler 1 Hamworthy Purewell classic auto 70 70 kw not rated Sn , SG04AIHGB31066 GAS SUPPLY CAPPED OFF Boiler 2 Hamworthy Purewell classic auto 70 70 kw not rated Sn , SG04AIHGN31067 burner pressure Low high - 2 mb High fire - 11 mb GFA Low fire 02 , 10.8 Co2 , 5.7 Co , 2 ppm Ratio , 0.0000 High fire 02 , 6.0 Co2 , 8.5 Co , 2 ppm Ratio , 0.0000

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6840
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6840
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6840
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6840
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6840
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes