## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Burn Promenade
Houghton-Le-Spring
County Durham
DH4 5EW
CARRIED OUT ON BEHALF OF
Castles & Coasts Housing Association
REPORT NUMBER: 21-6856
DATE OF REPORT: 16/06/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6856
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Castles & Coasts Housing Association
Address | Arcadia House
Balliol Business Park
Newcastle Upon Tyne
NE12 8EW
Site Address | Burn Promenade
Houghton-Le-Spring
County Durham
DH4 5EW
Carried Out On | 26/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
6 Month Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6856
SECTION 3: Report
LPC 26.4.21 0810 - 1115 Attended site and carried out 6 monthly mechanical check. Boilers and gas pipe work have not been tested or worked on today . Cold water booster set Grundfos HYDRO MULTI - E 2 CRIEO10 03 Product no , 98486773 Twin pump unit Expansion vessel charged to 5 bar ( 10 max) Both pumps ran to ensure smooth operation, air ways cleaned , vented as req No excessive vibration or leaks present . DHW Calorifiors x 2 ACV Jumbo 800 2015 date off manufacture Heating capacity- 125 L DHW storage capacity - 675 L Both cylinders have their own 3 port valves fitted , I cannot test these valves as the heads are missing. The valves would have been balanced and set up , no signs of leaking or corrosion present . The DHW draw off from both Calorifiors run into a Horne mixing valve , no signs of leaking or corrosion present . DHW Calorifior Expansion vessels x 2 Aquasustem VAV100 Pre charge pressure- 3.5 bar Checked charge pressure and found to be correct. No signs of leaks or corrosion present . DHW Calorifior Pressure Relief Valves x 2 Reliance Model - TPR28 Size 25 DN Pressure setting - 7 bar 90 - 95 C Rated discharge 50 KW DR DHW Secondary return pumps x2 Grundfos UPS 25 - 55 N 180 - 2 x speed Bronze . Both ran through all speeds working ok , no leaks or excessive vibration present. unions either side in good condition no leaks . DHW Primary Pumps Grundfos - Twin set Magna 1D 65 - 60 F340 230V Swapped over duties on control panel ,ran both heads to ensure against seizure , as no auto select function on panel Pumps have a Air Vent fitted , vented to clear any air in circuit . Went through pump head speed range , tested for excessive vibration . Both Isolation valves either side of pump , operating correctly fully isolating. Cleaned cooling fins CH 3 x port valve and actuator Actuator - E16 230A Controls are not wired up , so valve / actuator are adjusted manually, system does no auto compensate Valve not moved through positions, and system has been balanced- working ok . No leaks present, isolation valves on 2 x sides all working ok . CH pumps Grundfos twin set Magna 1D 65 - 120 F340 230V Swapped over duties via control panel , as no auto select function on panel , to prevent against seizure . Pumps have a vent installed , vented and cleared air from circuit . Ran both heads through full speed range , checked for excessive vibration- all ok No signs of leaks or corrosion present . Boiler shunt pumps 2 x Grundfos Magna 1D 40 120 F 230V Both heads ran through full speed range . No excessive vibration or leaks present . Pumps fo not have the facility to fit a vent key . Plate heat exchanger . In good condition, no cold spots present to the touch . No signs of leaking or corrosion present. Pressurisation unit CH JET . Mini 130D 230V Water staining present to internal case . Checked all function and settings found to be working ok . Would reccommed fitting a new ball valve, as water level very high in tank no adjustment left on arm . Filling loop is fitting for emergency or high speed filling of system. CH expansion vessel . Jet Contra flex 100 L Vessel has a local isolation valve and pressure relief valve inline . Checked charge pressure and found it to be correct as per manufacturers instructions- 1.5 bar No signs of leaks or corrosion present . CH expansion vessel prv G & S 3 Bar rating No signs of passing , leaks or corrosion present. Boilers 2 x potterton EC Three 215 E Both boilers working ok . No error codes on displays . No signs of leaks etc present on auto air vents or pressure relief valves .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6856
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6856
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6856
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6856
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6856
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes