## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Mackey Mews
Front Street
Stanley
DH9 0JE
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-6860
DATE OF REPORT: 16/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6860
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Mackey Mews
Front Street
Stanley
DH9 0JE
Carried Out On | 10/03/2021, 16/03/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
Responsive Repairs to External Contractors

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6860
SECTION 3: Report
Attend site so re commission heating 1245 No one on site all doors locked try to contact our office no one taking calls. Contact Darren Newbold who said he would get back to me , then rang Megan she also tried to find out who I could get access from. Travel to Greencroft to see if I could get the keys , no one knows where I can get them from. Contact James from karbon who told me to stand down until the keys were made avaliable. Offsite 1505 no access Attend site 0800 No access to all rooms needed until keys found, Find ideal w120 heating boiler being supplied by a g4 gas meter this cannot supply enough gas as per bs6644 so isolated and capped off ID Ideal logic 30 system boiler fed by 57 m of 40 mm trac pipe working pressure 18.6 mb all readings within manufacturer's recommended readings , boiler new and in good condition, condensate trap cleaned. Trac pipe travels in a sealed duct without ventilation this need addressed AT RISK Boiler room has no ventilation this has 1 no room sealed boiler heating buffer vessel and associated plant id advise fitting ventilation for cooling and has 3 gas meters in advise high and low ventilation AT RISK Keys need cutting to aid our access and a floor plan needs producing so people know where plant is located as at the min only a couple of people know where the plant is situated and in the event of a gas escape it could take to long to locate ECV

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6860
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6860
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6860
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6860
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6860
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes