## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
7 Stewart Court,
Chopgate
Middlesbrough
TS9 7JZ
CARRIED OUT ON BEHALF OF
HG Morgan Sindall
REPORT NUMBER: 21-6875
DATE OF REPORT: 24/05/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-6875
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | HG Morgan Sindall
Address | Sheffield South
Yorkshire
S9 2UB
Site Address | 7 Stewart Court,
Chopgate
Middlesbrough
TS9 7JZ
Carried Out On | 10/03/2021
Survey Completed By | Darren Reay
SECTION 2: Introduction
No heating or hot water. Wall controls not working customer advise electrician attended last night but was not able to do anything so he is still without heating and hot water Boiler. No covid -19 risk - Aware social dist - Vun elderly

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-6875
SECTION 3: Report
Attended site last night. Time on site 3hrs System was struggling to run and pulling out on high pressure( refrigerant cycle) After full investigation if the system it was found to be totally empty of any system water. Full system leak checked but no obvious signs of fluid leaks. The system comprises of a 10yr old mitsubishi ecodan connected to a boilermaker thermal store. Suspect pinhole to DHW coil and loosing system water to the DHW demand. The portable expansion vessel has failed and the boost immersion has also corroded and is no longer operating. The radiators to the property are undersized from the original installation. The client has experienced high billing of electricity for the duration of the installation. System filled and vented and education given to the client to manage the system while a decision is made. In my opinion the system is now unrepairable and has reached the end of its life. Recommend removal and installation of a replacement system. Ecodan with preplanned DHW cylinder. Radiators will also need to be upgraded. Approximate cost £11, 300 exc vat at 5%

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-6875
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6875
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6875
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6875
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-6875
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes