## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
1-37 Park View
Park Road
Lynemouth
NE61 5XL
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-7061
DATE OF REPORT: 13/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-7061
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | 1-37 Park View
Park Road
Lynemouth
NE61 5XL
Carried Out On | 13/04/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
The flow temperatures from the hot water outlets in the right hand side guest room have been repeatedly low as recorded by our water hygiene contractor. Please investigate and remedy possible causes.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-7061
SECTION 3: Report
Attend site 0800 Pick up parts from wholesalers x2 to allow alterations to DHW pipework to buffer vessel in the plant room as per recommendations from feasibility report . All dhw had to be drained in the plant room to allow the 67mm pipework to be altered. The old hot tie in from the hot flow was moved down from middle of the buffer vessel down to mix with the cold fill, a new 67mm nonecreturn valve was fitted to the cold fill and new isolated fitted. Vent taps where possible and check temp in room 37 find it to ne 47°C but this will increase as system heating up. Off site 1400 complete Parts used 1 no 67mm Street elbow 1 no 67mm elbow Both from Athlone Parts used from wholesalers 2 no 67mm straight connectors 2 no 21/2" flanges 1 no 21/2" none return valve 1 no 21/2" isolation valve 4 no 21/2" - 67mm connections 4 no 22mm elbows 2 no 22mm straights 1 x 67mm pipe 1 no 22mm pipe I bought these on job no 21- 7022

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-7061
SECTION 4: Photos
Room / Area
Description
Notes
New pipework installed with new valves
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7061
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7061
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7061
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7061
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes