## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Matfen Court
Chester Le Street
Durham
DH2 2 TX
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-7344
DATE OF REPORT: 21/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-7344
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Matfen Court
Chester Le Street
Durham
DH2 2 TX
Carried Out On | 08/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
No heating or hot water OOH CALL OUT

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-7344
SECTION 3: Report
LPC 8.4.21 0835 - 1110 Arrived on site and gained to plantroom area, found no demand to boiler ( only 1 x boiler running due to flue ) pumps not running all in flow failiure , no CH or DHW to building . Tested Trend controller , found to have power but non operational. Put all pumps into hand mode and got all running, locked boiler in hand mode and set at 65c as no valve control. Motorised valve to Calorifior and CH circuit, manually fully opened . Boiler running ok and will shut off one 65c is reached preventing, overheating DHW temp in calorifior . Notice attached to boiler stating- do not alter temperature settings. Image of controller has been sent to Multiphase to be identified for replacement. Monitored functions and performance of system , DHW upto 60c fully recovered and CH to building ok Boiler modulating and shutting down with temps .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-7344
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7344
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7344
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7344
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7344
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes