## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Shelley Court
Pelton Fell
Chester-le-Street
DH2 2QD
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-7440
DATE OF REPORT: 08/09/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-7440
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Shelley Court
Pelton Fell
Chester-le-Street
DH2 2QD
Carried Out On | 15/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Repairs needed following on from annual commercial gas safety inspection found boiler in.1 not to be running . Parts will be req

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-7440
SECTION 3: Report
LPC 15.4.21 1415 - 1630 Arrived on site and gained access to plantroom area. Carried out extensive fault finding on boiler no.1 LHS. Tested wiring harness , finally proved fault main PCB was cause of faults . Fitted new main PCB , new power relay PCB card and new storage key as per Remeha specifications. Set up peramiters and identify , allowed time to register . Created demand and tested all functions of appliance , found to be ok . Tested for safe operation as per manufacturers instructions, in both high and low fire modes . Monitored functions and performance of appliance all ok . Appliance details Boiler 1 LHS Remeha Quinta pro 115 Sn , 1025700508180 115 kw not rated GFA High fire 02 , 4.8 Co2 , 9.2 Co , 49 ppm Ratio , 0.0005 Low fire 02 , 6.4 Co2 , 8.2 Co , 12 ppm Ratio , 0.0001

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-7440
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7440
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7440
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7440
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7440
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes