## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
1-38 Moordale Court
Fabian Road
Middlesbrough
TS6 9RH
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-7509
DATE OF REPORT: 21/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-7509
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | 1-38 Moordale Court
Fabian Road
Middlesbrough
TS6 9RH
Carried Out On | 20/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Boiler fault e34 leaking no heat or hot water. Residents are reporting no heating or hot water. Boiler showing fault E24 and making an alarm sound. Leak on floor of boiler room. Urgent repair required.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-7509
SECTION 3: Report
LPC 20.4.21 1030 - 1620 Arrived on site and gained access to building , collected keys and proceeded to plantroom . Gained access to plantroom area , and found it to be literally flooded . Pressurisation unit was reading 3.3 bar and all PRV'S had lifted , but unit still attempting to fill. All 3 x boilers in various fault codes and not running . Shut down power supply to control panel and the area safe , to prevent further damage . Drained off excess pressure until system settled at 1.2 bar , brushed out water and made area safe to work in . Found cause of high pressure to be the 425 L CH CH expansion vessel as , no pressure at all present. Recharged with compressor, until correct charge achieved. Found that the vessel will req replacing asap, as small amount of water present in Schrader valve . Found that all 3 x boilers have suffered from water ingress , due to excessive pressure from Auto Air Vents Repaired leaks and attempted to get the boilers all running, but electrical components have been damaged. Finally managed to get boiler no.2 middle running , to supply DHW + CH. Both boilers 1 & 3 req fans and ignition transformers , parts orderd as req . The DHW to the building is supplied via 2 x unvented Calorifiors, both have immersion heaters fitted . The RHS Calorifior has a label on the immersion heater , stating do not use . As only 1 x boiler is running at the moment , I isolated the RHS Calorifior from the DHW circuit . One boiler would not be able to cope with 2 x Calorifior heat recovery and the CH to the building . With the LHS Calorifior only in use I turned on the immersion heater , and checked it to be sure its pulling current ( working ok ) Ran the boiler in just DHW demand and recovered the stored DHW temp to 60c as req . Pulled the DHW through to all taps in the building , entire building now has DHW . Locked the CH Belimo actuator in mid position to provide CH to the building, without comprising DHW pergormance . Checked all rads in the building , checked with flats to ensure they have heat . Each radiator has a TRV fitted so can be turned off if not req , as valve locked in manual mid position. Monitored functions and performance of temporary repair to system, found to be working ok . Site manager aware of situation . Checked DHW stored temperature after high usage found recovery to be ok and coping.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-7509
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7509
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7509
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7509
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7509
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes