## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Belle Vue Stadium
Delves Lane
Consett
DH8 7BF
CARRIED OUT ON BEHALF OF
Consett AFC
REPORT NUMBER: 21-7582
DATE OF REPORT: 23/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-7582
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Consett AFC
Address | Belle Vue Stadium
Delves Lane
Consett
DH8 7BF
Site Address | Belle Vue Stadium
Delves Lane
Consett
DH8 7BF
Carried Out On | 23/04/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
Job Description - Investigate water heater and pressurisation unit issues.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-7582
SECTION 3: Report
Attend site 1100 for cold water booster issues and hot water boiler issues Hot water boiler Attend to find hot water boiler not working using manufacturer's instructions carry out checks find condensate constantly running strip burner out and find heat excanger wet , this means the exchanger is pin holed and warwe from the heater is leaking into the burner into thr flue and ending up into the condensate trap. Contact hamworthy who have said thesre no parts to replace its a new heater needed. Put together a quote to replace the heater Keith Forster attended to see if the existing heating boiler could be unilised. The cold water booster unit was inspected and the no 2 pump found to be siezed, the unit was isolated and drained down and no 2 pump stripped out and the spindal freed off, the pump was reassembled and tested and found to be ok. Ran the pump to check no leaks from the gland but all ok Offsite 1400 quote for newcwater heater

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-7582
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7582
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7582
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7582
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7582
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes