## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Renwick House
Abbey Meadows
Kirkhill
NE61 2BN
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-7718
DATE OF REPORT: 05/05/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-7718
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Renwick House
Abbey Meadows
Kirkhill
NE61 2BN
Carried Out On | 05/05/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Urgent flue repairs - following on from service.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-7718
SECTION 3: Report
LPC 5.4.21 1030 - 1630 Whilst on site working out the gas pipe work volume, I noticed a lot of condensate dripping from the flue . Upon closer examination I found that the flue was perforated in various areas, causing high volumes of condensate to leak . The 3 x ideal evomax boilers are fitted to a common flue , so theres a lit of condensate being produced . I attempted to repair the flue , but the material was beyond repair and falling to pieces when touched . The only solution was to removed the flue above boilers 1 & 2 , and shorten the flue . Boiler no.3 is now on the flue on it's own and the flue has been altered to suite along with condensate lines. Tested for safe operation and found the flue to working ok , no leaks present . Carried out GFA on boiler no.3 and found to be operating as per manufacturers instructions. Boilers 1 & 2 have their gas supply capped off and a zip tie through their isolators . Monitored functions and performance of boiler 3 and the flue all ok . This is only a temp solution as only 1 x boiler left running. Boiler 3 Ideal Evomax 80 GFA High fire 02 , 4.6 Co2 , 9.2 Co , 101 ppm Ratio , 0.0011 Low fire 02 , 5.4 Co2 , 8.8 Co ,21 ppm Ratio ,0.0002 Warning notice issued for boilers 1 & 2 / labels attached . Boiler no.3 has been locked into winter mode and controls put into hand . Checked the CH throughout the building and found to all be ok .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-7718
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7718
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7718
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7718
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7718
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes