## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
1-38 Moordale Court
Fabian Road
Eston
TS6 9RH
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-7783
DATE OF REPORT: 09/06/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-7783
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | 1-38 Moordale Court
Fabian Road
Eston
TS6 9RH
Carried Out On | 10/05/2021, 09/06/2021
Survey Completed By | Graham Parker
SECTION 2: Introduction
Building has no Heating hot water - call out made on Sunday evening around 9.30pm. Tenants at number 34 & 30 have called to say it has gone off again this morning. ----

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-7783
SECTION 3: Report
LPC 10.5.21 1510 - 1630 After attending site earlier today and re - programmed the peramiters in the pressurisation unit . The unit failed again and was looking for pump no.2 , that does not exist . Bypassed Interlock to control panel , causing nuisance lockouts ( terminals 1 + 2 linked together ) Isolated pressurisation unit and installed a filling loop , as an emergency measure. System now working ok , no issues as pressurisation now isolated and not interlocked to system. Pressurisation unit details Flamco Midi 125D Article code - 17460 240 v Single pump unit . On checking plant room found boiler pressurisation unit isolated and also fault lights on control cabinet. Checked boiler found fan was required. Recommissioned pressurisation unit. And also faulty pump

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-7783
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7783
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7783
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7783
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-7783
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes