## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Rooms within House, Strathmore House
163 Strathmore Crescent
Newcastle upon Tyne
NE4 8UA
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-8214
DATE OF REPORT: 17/06/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-8214
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Rooms within House, Strathmore House
163 Strathmore Crescent
Newcastle upon Tyne
NE4 8UA
Carried Out On | 08/06/2021,, 09/06/2021, 14/06/2021, 15/06/2021, 17/06/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
Commercial Boiler Repair - No Hot Water Graham Parker attended for Zenith on the 02/06/2021 and suggests this is an electrical issue - something tripping the emersion heater circuit.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-8214
SECTION 3: Report
Attend site 08/06/21 for no hot water, find gas boilers been switched of and no emersion , site only want hor water on but no heating so the only way thy can control the heating is by turning the boiler stats down this then kills the primary circuit to the hot water. The primary circuit needs altering so that the primary circuit can be ran when heating pumps are turned off , also find that there is no emersion on the calorfier Attend site 0745 09/06/21 Isolate and drain down heating system to allow alterations to the flow pipework feeding the primary circuit once altered fill and vent system, had to fit auto air vents to allow the air to be cleared , commission and test Clear all air lock m but these take most of the day as they keep tripping the boilers as the flow is interrupted. There are no controls for the heating or the hot water only the boiler stats advice fitting controls Offsite 1400 complete Attend site 1300 for heating still on after works carried out last week. Gain access and find t Heating gravitating through the pipework when hot water on . A 11/2" 2 port valve needs installing on the heating pipework after the pump and wired into a room stat also the electrical supply to be altered to allow the heating and hot water to work independently , I will reattend tomorrow to install the 2 prt valve and the the electrical works can be carried out. I've isolated the pump isolation valves to stop the heating g to gravitate around the system. Offsite 1500 fow Attend site 1145 15/06/21 Isoate and drain heating system , instal 11/2" 2 port valve after heating pumps and re route the heating flow and ad an automatic bypass , disconect the primary pump and pipe out. This now enables the system ro run like a s plan heating system and now hot water can work independently from the heating an proper controls be added so the heating can be switched off without having to turn down the boiler stat. Jim Shanley to alter the electrics and add a room srat to enable the heating to be turned on / off Offsite 1715 Attend 1000 17/06/21 to meet with leak from multiphase to sort out the wiring issues for the heating. Offsite 1100

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-8214
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8214
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8214
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8214
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8214
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes