## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
15 Moorcroft
Bowman drive
Dudley
Ne13 7FF
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-8368
DATE OF REPORT: 17/06/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-8368
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | 15 Moorcroft
Bowman drive
Dudley
Ne13 7FF
Carried Out On | 13/06/2021, 14/06/2021, 15/06/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
No Heating

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-8368
SECTION 3: Report
E05 fault on boiler 2, reset and all working, had to locate keys for boiler room first Attend site 0930 Find primary three port actuators shut, had to disconnect from electrical supply and manually open to get hot water on , BMS is not work and all equipment running on manual so instruct Adam from multiphase to attend investigate. Boiler 2 has a fault carry out tests but had to contact manufacturer who said to change the flow return thermisters, pick up from wholesalers and return to site , fit parts and test but find boiler sitting on status 8 which means flow and return temp to different, isolate boiler and drain down strip pump down and find pump impeller completely smashed so the boiler had no flow order the pump will fit it tomorrow Parts used 2 no flow return thermisters Offsite 1300 Attend site 0830 after picking up new pump from wholesalers Try to isolate water to heating boiler no 2 but find isolation valves not turning off so had to drain plantroom down , strip out pump underneath boiler and replace with new. Fill and vent system and test no 2 boiler now working and all faults cleared. All ok Parts used 1 no remeha pump Plant room all working apart from no 1 primary pump which is waiting for a replacement. Offsite 1100

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-8368
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8368
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8368
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8368
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8368
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes