## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Victoria Court
Front Street
Cullercoats
NE30 4QR
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-8528
DATE OF REPORT: 23/06/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-8528
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Victoria Court
Front Street
Cullercoats
NE30 4QR
Carried Out On | 18/06/2021, 21/06/2021, 22/06/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
SHO has reported that there is no hot water at Victoria Court. Please treat as urgent.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-8528
SECTION 3: Report
On arrival no Warden on site and difficulties gaining entry. Eventually got in and enquired regarding the report of no hot water. The residents informed me that the hot water had been off in the morning but had come back on during the day. Tested the hot water and it was working. It would appear that the stored hot water had been used up and the supply had recovered. Working on leaving. Attend site 1500 21/06/21 Find primary pump flow switch fault light on, check and find no water in the system, trace pipework back to pressurisation unit switched off , turn this on and find water leaking from inside. Open unit up and find both pumps leaking from the body so the heating pressure must have be dropping and the pump constantly running so some one has turned off the unit. I've isolated the out let to the unit and manually topped up the system using the quick fill , the flow switch light is now off and the primary circuit is at 70° and heating the DHW up. This is only a temp measure and a new pressurisation unit is needed Parts required 1 no midiflow pressurisation unit £870 (total pumps) 1 no pipework alterations £50 4 hours labour I'm not sure the pipework will be the same on the new unit so might require so minor pipework alterations to install Offsite 1630 fow Pick up new pressurisation unit and attended site 1245 Isolate and drain heating enough to install a new 15mm isolation valve. Once installed drain down the faulty pressurisation unit and strip out electrical supply. Strip out unit alter inlet and outlet pipework fit new unit to the wall , pipe up altering both pipes to allow installation and strip out existing electrics and install new as cables arnt long enough to fit to new unit. Commission unit , had to take advise on the wiring as the signal cables arnt labled up and I couldn't get unit to run once altered unit now up and running and system topping its self up. Parts used 1 no flanco single pump unit 1 no 15mm copper pipe van stock £16 4 no 15mm pressfit elbows van stock £8 1 no 20mm stuffing glad van stock £1 1 no 2.5mm 3 cor flex van stock £5 1 no 15mm isolation valve offsite 1630 complete

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-8528
SECTION 4: Photos
Room / Area
Description
Notes
Both pumps leaking allowing the heating system to loose pressure
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8528
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8528
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8528
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8528
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes