## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Southgate Court
Camsey Close
Longbenton
NE12 8UW
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-8741
DATE OF REPORT: 30/07/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-8741
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Unit 1 Hunslet Trading Estate
Servern Way
Hunslet
Leeds
LS10 1BL
Site Address | Southgate Court
Camsey Close
Longbenton
NE12 8UW
Carried Out On | 29/06/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
AGSC - TD 13/07/2021 - Last years certs have been sent over via email

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-8741
SECTION 3: Report
Attended site to carry out an annual ppm on all plant 3 no hamworthy fleet f150v heating boilers stripped cleaned reassemble and test used 3 x burner gaskets from van stock commission and test all ok no issues 2 no hamworthy p500 calorifiers operational checks no issues 1 no grundfos ups 32-80 n 180 dhw circulation pump operational check 0.90 amps no issues 1 no grundfos magna 3d 40-150 f250 twin set zone 1 heating pumps no issues 2 amps 1 no grundfos magna 3d 40-120 f250 twin set zone 2 heating pump no issues 1.75 amp 1 no grundfos magna 3d 32-100 180 twin set primary pumps no issues 1.3 amps 4 no zone valves operational check all ok no issues 1 no hamworthy 500l expansion vessel checked pressure is at 1.5 bar all ok 2 no hamworthy 60l dhw expansion vessel checked pressure in no 1 is at 3bar but no 2 is damaged needs replacing 1 no hamworthy chesil pressurisation unit operational checked all ok no issues Tightness test carried out 2-6-2 no issues all ok To bring plant up to 100% the expansion vessel off the domestic hot water needs replacing ive supplied a quote to Admin account.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-8741
SECTION 4: Photos
Room / Area
Description
Notes
Burners stripped out and washed
Room / Area
Description
Notes
All heat exchangers stripped and cleaned
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8741
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8741
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8741
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8741
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes