## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Whinstone Lodge
Front Street
Whitley Bay
NE25 8DJ
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-8834
DATE OF REPORT: 01/07/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-8834
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Whinstone Lodge
Front Street
Whitley Bay
NE25 8DJ
Carried Out On | 30/06/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
Pipes in foyer are making loud noises (like helicopter)

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-8834
SECTION 3: Report
Attend site 0800 for noisey pipework Gain access to various flats and when there heating is off the heating manifolds are banging , gain access to plant room and find every pump running on maximum and the pressure gauges are bouncing around. Turn all the plant off and switch each pump on one by and and comission No 1 heating pump magna 3 d 40-120 f 250 set to constant pressure at 6mtr head pump is working and not chattering No 2 heating pump magna 3 d 40- 120 f 250 won't reset its saying it has an internal fault and defaults to maximum output which is hammering the pipework, switch off and quote to replace as per conversion with grundfos technical No 1 ashp secondry pump grundfos magna 3 d 32-40 180 set to constant pressure at 4 mtr head pump is working No 2 ashp secondary pump grundfos magna 3 d 32-40 180 display is damaged and can't be set up quote to replace this pump as per grundfos technical, Heating now working without hammering Quote for replacement pumps Offsote 1100

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-8834
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8834
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8834
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8834
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8834
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes