## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
1-29 Langley House
Redcar
North Yorkshire
TS10 4JF
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-8835
DATE OF REPORT: 30/06/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-8835
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | 1-29 Langley House
Redcar
North Yorkshire
TS10 4JF
Carried Out On | 30/06/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
No heating. Tenant from flat 15 has called and said no one has any heating at all.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-8835
SECTION 3: Report
Attend site 1230 for no heating or hot water Find no 2 boiler isolated gas and electric when I arrived. Investigate fault trace to shunt pump siezed and tripped, isolate the pump and drain down strip out head and find impeller stuck gently free off and reassemble fill up and commissioned pump now running and heating now on. Find vt pump no 2 grundfos upsd 40-60 f siezedtried to free this off but its solid new pump needed this pump is no longer available and would need a new twin set to replace it with. Also find constant temp pump no 2 faulty carry out tests and find it has lost its electrical supply carry out fault finding but without tracing the supply throughout the plant room back to the panel I'm unable to find the fault( panel looks like its been worked on before and is in poor condition so I'd recommend a controls engineer to carry out these works as the satchwell controls in the panel are ancient and very brittle. Price for replacement pump £1130 + vat Offsite 1430 heating and hot water now on heating only has one pump working

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-8835
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8835
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8835
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8835
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8835
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes