## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
4 Chapelville
Front Street
Seaton Burn
NE13 6EH
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-8994
DATE OF REPORT: 09/07/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-8994
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | 4 Chapelville
Front Street
Seaton Burn
NE13 6EH
Carried Out On | 08/07/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
Banging noise coming from pipes when heating is on. - Suspected airlock....

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-8994
SECTION 3: Report
Find manifold chattering when closed open all actuators and heating quietens, but the water flow through the manifold is too high , gain access to plant room and find heating pumps on maximum and making all components chatter, contact grunfos to find how to unlock the controls and once unlocked switch pumps on to auto adapt which brought thr head m3 fro 15m3 to 3.5 m3 and pipework all quiet Return to flat and all quiet

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-8994
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8994
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8994
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8994
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-8994
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes