## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Victoria Court
Front Street
Cullercoats
NE30 4QR
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-9063
DATE OF REPORT: 30/07/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-9063
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Unit 1 Hunslet Trading Estate
Servern Way
Hunslet
Leeds
LS10 1BL
Site Address | Victoria Court
Front Street
Cullercoats
NE30 4QR
Carried Out On | 15/07/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
AGSC

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-9063
SECTION 3: Report
Attend site 0800 Find no 1 and 3 boilers in fault , strip all three boilers down and find 1 and 3 ignition probes corroded away travel to wholesalers to collect new parts. Return to site strip and clean all 3 boilers and replace 3 x burner gaskets and 3 x ignition probes commission all ok set up to manufacturer's specification Boiler no 1 remehra quinta 115 stripped cleaned and gasket and probes replaced poor condition Boiler no 2 remehra quinta 115 stripped cleaned and gasket and probes replaced poor condition Boiler no 3 remehra quinta 115 stripped cleaned and gasket and probes replaced poor condition Flamco digi fill pressurisation unit operational check all ok Grundfos magna 3d 40-100 f220 primary pump twin set operational check all ok Grundfos magna 3d 40-120 f250 v t pump twin set operational check all ok Schneider heating zone valve unable to test operational as bms isn't working Schneider calorfier no 1 hot water valve unable to test operational as bms isn't working Schneider calorfier no 2 hot water valve unable to test operational as bms isn't working Grundfos alpha 2 15-50 dhw pump operational check all ok Calorfier no 1+2 hamworthy ps 400 visually checked no leaks observed both working ok 2 x 300 ltr heating expansion vessels isolated and drained pressure set to 1.5 bar 4 x hamworthy 25 ltr dhw expansion vessels drained and pressure set 3.5 bar All pipework checked and in good working order with no leaks and lagging in ok condition Advice multiphase to attend to getvthe bms system working correctly as at the minute every thing is working in manual and valves manually opened Offsite 1430 complete

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-9063
SECTION 4: Photos
Room / Area
Description
Notes
New ignition probes next to existing
Room / Area
Description
Notes
Boilers all stripped and cleaned
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9063
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9063
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9063
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9063
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes