## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
1A Fellsdyke Court
Gateshead
Tyne & Wear
NE10 9SB
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-9147
DATE OF REPORT: 28/07/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-9147
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | 1A Fellsdyke Court
Gateshead
Tyne & Wear
NE10 9SB
Carried Out On | 28/07/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
The radiator in the communal sitting room cold - Can we raise a job for the contractor who deals with the communal heating for these properties. ---- There appears to be nothing wrong with the valves on the radiator and unable to find a zone valve/isolation to the flat to check if that's the problem with some of the radiators not heating.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-9147
SECTION 3: Report
Attend site 1430 for radiators not working Search flat find boxing in in bedroom cuboard strip this out and find 2 port valve and actuator behind check operation of both and find ok reassemble boxing in and go to plantroom , intergate the bms and find when outside temperature is 20° the VT circuit is only asking for 35° so there's no heating on. Adjust the 20° set point so that it gives 50° flow temperature save the settings and wait until temperature flows in to the flats radiators all ok now and the tennant can regulate his temperature using his room stat. Offsite 1630 complete

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-9147
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9147
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9147
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9147
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9147
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes