## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Trinity Court - Block 1-16
Roman Way
Corbridge
NE45 5JN
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-9242
DATE OF REPORT: 19/07/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-9242
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Trinity Court - Block 1-16
Roman Way
Corbridge
NE45 5JN
Carried Out On | 19/07/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
Yasemin called to report heating running hot to ground floor - Yasemin called to report heating running hot to ground floor flats & corridoor - reported by tenant flat 1 No error mesaage on boiler can the heating be turned down

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-9242
SECTION 3: Report
Attend site 1445 for over heating through out Gain access to manifold's and check not passing but all ok no leaking giacomini cartridges, gain access to plant room and find 3 port vt valve open and putting heat into the building, check DC voltatge input to vt actuator and find 10v (this means calling for heat) investigate and find bms asking for inside temp of 28°and outside temp shutvoff of 28° also vt minimal temp of 55° these are wrong. Reset indoor target temp of 21° Reset outdoor maximum temp of 21° And a minimum flow temp of 30° This has closed the heating vt valve and shut the pumps down heating is now off

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-9242
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9242
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9242
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9242
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9242
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes