## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Communal Area
Oakwood Court (1-30)
Stanley
DH9 8NE
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-9963
DATE OF REPORT: 21/09/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-9963
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Communal Area
Oakwood Court (1-30)
Stanley
DH9 8NE
Carried Out On | 11/08/2021, 12/08/2021, 12/08/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
Leak in laundry room. From boiler room

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-9963
SECTION 3: Report
Attend site 1430 for a leak in plant room, Investigate and find no 2 pump on pressurisation unit leaking from body and leaking onto floor and finding is way down to laundry order pump. Offsite 1545 fow 12/8/21 attend 0800 Pick pump up from wholesalers travel to site Isolate and drain pressurisation unit down strip out old pump hadcto to take out expansion vessel as access is very tight. Alter pipework as old pump is obsolete and new pump has different connections, once piped up reassemble the rest of unit , fill and vent , whilst commissioning notice the plastic 't' on the other pump which has the expansion vessel connected to it is leaking. Isolate and drain down again and strip out the t find each of the connections have cracked, when the unit is off the heating won't operate so have to link bms controls out to get heating to run and go to wholesalers to collect parts to enable the unit to be recommissioned. So using 2 x 1/2" bsp 't's 2 x 1/2" close taper nipples 1 x m/r elbow and a 1/2"-3/8" reducing bush, repipe the the pumps up deleting the damaged plastic t , once fitted commission and test reconnect the bms test all ok. Parts used 1 no pump total pumps 1 x fittings bsmiths brothers Onsite 0800 till 1200 then 1530 till 1700 complete

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-9963
SECTION 4: Photos
Room / Area
Description
Notes
New pump fitted
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9963
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9963
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9963
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-9963
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes