## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Flat 3 Pembroke Court
Hylton Lane
Downhill
SR5 4DF
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 22-14740
DATE OF REPORT: 18/01/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-14740
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Flat 3 Pembroke Court
Hylton Lane
Downhill
SR5 4DF
Carried Out On | 18/01/2022
Survey Completed By | Rhys Brown
SECTION 2: Introduction
Flat 3 heating wont turn off - Been on 24/7

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-14740
SECTION 3: Report
When attending flat was very hot (27 degrees) looking in cupboard noticed that the power going to the two port valve working correctly and when removing the head the spindle was freely turning, there for meaning the head from the valve was broken. Purchased new valve (Honeywell V4043H1056) from wolsley Sunderland with the job number as reference. Replaced and wired in the valve head. Heating now working as it should. Boiler in laundry- Boiler on E1 fault code which means pressure is low or it is overheating. When resetting the boiler it will fire up but only for approx 5 minutes from start up to overheating. Checked all rads to which were all open. Trv head was broken on one rad, (Pegler terrier trv head to be replaced). After opening the valve boiler had still got up to temp knocking its send off at 67 degrees when boiler set at 80. The rads near the boiler are getting hot but rads further along on the leg are not heating up at all.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-14740
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-14740
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-14740
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-14740
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-14740
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes