## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Southgate
Mendip Close
Longbenton
NE12 8UW
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 22-14789
DATE OF REPORT: 15/03/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-14789
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Southgate
Mendip Close
Longbenton
NE12 8UW
Carried Out On | 09/03/2022,, 15/03/2022
Survey Completed By | Graham Parker
SECTION 2: Introduction
6 Month Mechanical Check - TD Feb 2022

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-14789
SECTION 3: Report
Called to carry out ppm check on southgates 3 x Hamworthy Fleet f150v boilers = 2 operational and 1 in fault requiring a pump and flow switch and condensate trap broken 2 x Hamworthy powerstock 500l calorifiers = both operational 2 x dhw expansion vessels = both operational and charged to 3.5 bar 1 x heating expansion vessel = operational and charged to 1.6 bar Flue = good condition Flue condensate = leaking in sections 1 x gas interlock = operational Lagging in good condition 1 x Hamworthy chessil pressurisation unit = operational and no faults 7 x prv,s operational and not passing 2 x schnieder m700 actuators = operational 2 x schnieder hot water actuators = operational 2 x zone 1 pumps Grundfos magna3d 40-120 pump 1 = good = 0.2 amps pump 2 = good = 0.2 amps 2 x zone 2 pumps Grundfos magna3d 40-150 pump 1= good =0.2 amps pump 2 = good =0.2 amps 2 x primary pumps Grundfos magna3d 32-100 pump 1= good =0.5 amps pump =2 good = 0.6 amps 2 x destrat pumps biral pump 1= good = 0.3 amps pump 2= good = 0.3 amps 1 x secondary return pump Grundfos 32-80 = good= 0.7 amps

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-14789
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-14789
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-14789
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-14789
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-14789
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes