## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
5 Whinstone Lodge
Front street
North Tyneside
Ne25 8DB
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 22-15845
DATE OF REPORT: 24/02/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-15845
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | 5 Whinstone Lodge
Front street
North Tyneside
Ne25 8DB
Carried Out On | 19/02/2022,, 22/02/2022
Survey Completed By | Graham Parker
SECTION 2: Introduction
No Heating / HW

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-15845
SECTION 3: Report
DH - 19/2/22 - attended flat 5 to find 20 degree flow temperature at the manifold. Investigation within the plan t room revealed a pressurisation unit fault which was holding the boilers and pump sets off from operating. Once the low pressure switch was satisfied plant fired back into operation. Follow on works to investigate hamworthy chesil pressurisation unit on LTHW circuit. 22/02/22 After investigation found pump was running very very hot on LTHW pressurisation unit and was trying to fill system. Opened up bleeding screw and found pump was full of air so vented and pump started to empty cold fill tank and put water in to system. Altered pressure switches to fill to 1.5 bar low pressure alarm to 0.7 and high pressure alarm to 2.7

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-15845
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-15845
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-15845
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-15845
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-15845
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes