## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Mayfield Park
Bristol Drive
Battle Hill
NE28 9BF
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 22-16560
DATE OF REPORT: 28/03/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-16560
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Mayfield Park
Bristol Drive
Battle Hill
NE28 9BF
Carried Out On | 25/03/2022
Survey Completed By | Graham Parker
SECTION 2: Introduction
6 Month Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-16560
SECTION 3: Report
Called to carry out ppm check On arrival found numerous issues with the plant = boiler 2 faulty ASHP plate ex pump 2 in fault, ASHP pressurisation unit in fault 2 x Hamworthy Fleet f150v = 1 operational. Water from the rear sump seal has leaked 2 showing limit stat fault .Water has dropped onto this 2 x lochinvar eco shielddirect fired units = 1 operational 2 operational 2 x wilo pressurisation units 1 = operational 2 = faulty= Now rectified issue was blocked transducer OPERATIONAL NOW 2 x DHW expansion vessels 1 = repressurised to 3.0bar 2 = repressurised to 3.0 bar 1 x C/H expansion vessel = repressurised to 1.5 bar System pressure charged to 1.5 bar Flue good on boilers Flue on water heaters ok apart from the flue appliance connectors Leak on condensate from Flue from boilers Lagging good Gauges good Gas interlock good PRV,S x 5 = operational 2 x schnieder actuators = operational 2 x Grundfos MGE80 zone 2 heating pumps 1= operational 0.5 amps 2 = operational 0.7 amps 2 x Grundfos magna3d 40-120 zone 2 heating pumps 1 = operational 0.4 amps 2 = operational 0.6 amps 1 x secondary return pump Grundfos alpha2 15-50 1= operational 0.3 amps 2 x Grundfos magna3d 32-80 plate heat exchanger pumps 1 =operational 0.3 amps 2 = operational 0.3 amps 2 x Grundfos magna3d 40-160 ASHP primary pumps 1 = operational 2.1 amps 2 = faulty

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-16560
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16560
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16560
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16560
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16560
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes