## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Carville House
Carville Road
Wallsend
NE28 6DX
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 22-16562
DATE OF REPORT: 24/03/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-16562
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Carville House
Carville Road
Wallsend
NE28 6DX
Carried Out On | 23/03/2022
Survey Completed By | Graham Parker
SECTION 2: Introduction
6 Monthly Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-16562
SECTION 3: Report
Called to carry out ppm check 3 x Hamworthy Fleet f125v = 1 operational 2 operational 3 operational 2 x Hamworthy powerstock calorifiers = 1 operational 2 operational 1 x Hamworthy chessil pressurisation unit = operational 2 x DHW expansion vessels 1 = repressurised to 3.5 bar 2 = repressurised to 3.5 bar 1 x C/H expansion vessel = repressurised to 1.5 bar System pressure charged to 1.5 bar Flue has 1 leaking seal allowing condensate to weep Fixed Leak on condensate bottle trap from Flue Lagging good Gauges good 1 temperature gauge faulty Gas interlock good PRV,S x 8 good except 1 dn25 3.2 bar is passing slightly 4 x schnieder actuators = operational 2 x biral destrat pumps 1 = operational 0.3 amps 2 = operational 0.3 amps 4 x Grundfos magna3d 32-80 heating pumps 1= operational 0.4 amps 2 = operational 0.4 amps 3 = operational 0.3 amps 4 = operational 0.5 amps 2 x Grundfos MGE80A 1-56C primary pumps 1 = operational 0.6 amps 2 = operational 0.5 amps 1 x secondary return pump Grundfos magna1 25-80 1= operational 0.4 amps requires to be turned to a horizontal position

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-16562
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16562
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16562
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16562
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16562
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes