## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Tindale Drive
Fellside Park
Whickam
NE16 4HX
CARRIED OUT ON BEHALF OF
Castles & Coasts Housing Association
REPORT NUMBER: 22-16568
DATE OF REPORT: 27/04/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-16568
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Castles & Coasts Housing Association
Address | Arcadia House
Balliol Business Park
Newcastle Upon Tyne
NE12 8EW
Site Address | Tindale Drive
Fellside Park
Whickam
NE16 4HX
Carried Out On | 27/04/2022
Survey Completed By | Graham Parker
SECTION 2: Introduction
6 Month Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-16568
SECTION 3: Report
3 x Hamworthy purewell = 2 operational and 1 isolated 1 x acv greenline calorifier = operational condition poor Flue ok no leaks Flue fan = operational 0.72 amps 1 x flamco pressurisation unit = operational 1 x gas interlock = operational All Gauges and valves = operational Lagging = average No visible water leaks 1 x xpot compact system filter = requires new filter 1 x aecv handle present 1 x heating expansion vessel = operational charged to 1.5 bar 1 x DHW expansion vessel = operational and charged to 2.7 bar 2 x 3 port mixing valves = operational but showing signs of leaking on spindle 2 x Siemens actuators = operational 2 x vt pumps =1 Grundfos 40-60 = operational 1.3 amps. 2 wilo yonos max 40 = operational 1 amps 2 x primary pumps = 1 Grundfos 40-60 = operational 0.8 amps. 2 wilo yonos maxo 40 = operational 1 amps 1 x secondary return pump Grundfos ups 40-50 = operational 0.5 amps

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-16568
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16568
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16568
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16568
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16568
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes