## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Burn Promenade
Houghton-Le-Spring
County Durham
DH4 5EW
CARRIED OUT ON BEHALF OF
Castles & Coasts Housing Association
REPORT NUMBER: 22-16569
DATE OF REPORT: 26/07/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-16569
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Castles & Coasts Housing Association
Address | Arcadia House
Balliol Business Park
Newcastle Upon Tyne
NE12 8EW
Site Address | Burn Promenade
Houghton-Le-Spring
County Durham
DH4 5EW
Carried Out On | 28/04/2022
Survey Completed By | Graham Parker
SECTION 2: Introduction
6 Month Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-16569
SECTION 3: Report
2 x potterton euro condense three = operational 2 x acv jumbo 800 calorifiers = good and operational Gauges and valves = operational Flue = signs of leaking Pipe work = good 1 x plate heat exchanger = operational Gas interlock safety system disabled 1 x AECV = handle present but stiff 1 x jet pressurisation unit =operational 2 x DHW expansion vessels = operational and charged to 3.5 bar 1 x heating expansion vessel = operational and charged to 1.5 bar Water test carried out = water discoloured and PH 8.1 @ 16 degrees 2 x vt pumps Grundfos magna1 65-120 =1 good 2 amps. 2 = good 2 amps 2 x primary pumps Grundfos magna1 65-60 = 1 good 0.7 amps =2 good 0.7 amps 2 x secondary return pumps Grundfos ups 25-55 = 1 good 0.5 amps =2 good 0.5 amps 1 x TMV off calorifiers = operational and set to 60 degrees 2 x 3 port mixing valves manual DHW= operational 1 x 3 port mixing valve = operational 1 x actuator = operational Condensate pipe leaking

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-16569
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16569
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16569
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16569
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-16569
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes