## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Carlton Court
Scorer Street
North Shields
NE29 0LB
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 22-18865
DATE OF REPORT: 31/05/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-18865
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Carlton Court
Scorer Street
North Shields
NE29 0LB
Carried Out On | 31/05/2022
Survey Completed By | Graham Parker
SECTION 2: Introduction
Mechanical Check / 6 Monthly

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-18865
SECTION 3: Report
Arrived on site to carry out ppm 3 x Hamworthy Fleet f125v boilers 1= operational 2= was in fault on arrival this reset and is operational 3 = operational 2 x Hamworthy powerstock calorifiers 1 = operational and good 2= operational and good 1 x Hamworthy chessil pressurisation unit = operational but since last reset has made up system water by 831 litres suggesting there is a water leak somewhere , I carried out a visual check around building but nothing obvious. 1 x heating expansion vessel = good charged to 1.7 bar 2 x DHWS expansion vessels = good charged to 3.5 bar 3 x Siemens m700 actuators and 3 port valves = good = operational Lagging = good Valves = operational Sensors and Gauges = operational Condensate pipe work is leaking and requires replacement 1 x gas interlock = operational Water test results PH6.9 @ 20 degrees 2 x biral de strat pumps 1= operational 0.3 amps 1 x Grundfos magna3 25-60 secondary return pump = operational 0.2 amps 2 x Grundfos magna3d 40-150 primary pumps 1 = operational 0.7 amps ,2= operational 0.7 amps 2 x Grundfos magna3d 50-180 vt pumps 1= operational 0.2 amps , 2 = operational 0.2 amps Further investigation will be required to accertaine the location and reasoning for the constant operation of the pressurisation unit

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-18865
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-18865
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-18865
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-18865
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-18865
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes