## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Eccles Grange
Church Road
Backworth
NE27 0FW
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 22-20441
DATE OF REPORT: 06/10/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-20441
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Eccles Grange
Church Road
Backworth
NE27 0FW
Carried Out On | 05/07/2022, 06/07/2022
Survey Completed By | Graham Parker
SECTION 2: Introduction
6 Monthly/Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-20441
SECTION 3: Report
Carried out 6 monthly checks on plant Boilers 2x Hamworthy f250v 1 = in lock out requires flow and return sensors 2 = operational Pressurisation unit Hamworthy chesil- V2- 738.5 = operational 2 x Hamworthy powerstock calorifiers = good LTHW pumps 2 x wilo d40/1-12. 1 = operational - 0.4 amps. 2 = operational. 0.4 amps DHW Primary pumps 2 x wilo d40/1-12. 1 = operational 1.2 amps. 2 = operational. 1.2 amps HWS Secondary Pump 1x wilo pico-z25/1.6. 0.2 amps Destrafication pumps 2x biral -3110. 1 =operational. 0.3 amps. 2 = operational. 0.3 amps Hot water expansion vessels 2x reflex de60 60ltr pressurised to 3.6 bar Boiler expansion vessel 1x refix de60 200ltr Pressurised to 1.5bar Pipe work has leaks on the CWS shut off valve CWS check valve and on the secondary hot water inlet. Also a leak on the heating flow going into the building. Lagging = average Flue = good Sensors are not registering on the BMS HMI Gas solenoid = operational Acuators x 3 = operational Gauges x 13 = 2 temperature gauges faulty Valves = operational

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-20441
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-20441
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-20441
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-20441
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-20441
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes