## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Rosebank Hall
Willington Terrace
Wallsend
NE28 7BT
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 22-21180
DATE OF REPORT: 06/10/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-21180
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Rosebank Hall
Willington Terrace
Wallsend
NE28 7BT
Carried Out On | 21/07/2022
Survey Completed By | Graham Parker
SECTION 2: Introduction
6 Monthly / Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-21180
SECTION 3: Report
Carried out pr planned maintenance check 3 x remeha quinta Pro 115. 1= operational 2= operational 3= operational 2 x remeha calorifiers. 1= operational 2= operational 2 x DHW expansion vessels 1= operational charged to 3.5 bar 2= operational charged to 3.5 bar 1 x CH expansion vessel = operational. Charged to 3.5 bar 1 x flamco pressurisation unit = operational 1 x gas interlock = operational Lagging average All Gauges operational 2 x Siemens actuators = operational 2 x 3 port mixing valves = operational 7 x prv,s 6 operational and 1 DN25 3.5 bar cold water passing Condensate pipe unblocked Water sample = PH7.8 @ 38 degrees Flues ok Valves showing bad signs of leakage 1 x secondary return pump Grundfos magna 32-100 = operational 0.3 amps 2 x primary pumps Grundfos TPE 50-180. 1 = operational 1.2 amps 2 = operational 0.9 amps 2 x vt pumps Grundfos TPE 50-240. 1= operational 1.1 amps 2= operational 1.3 amps both require new bearings 2 x destrat pumps Grundfos comfort. 1= operational 0.3 2= operational 0.3 amps

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-21180
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-21180
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-21180
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-21180
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-21180
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes