## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Patton House
Patton Walk
Wheatley Hill
DH6 3QX
CARRIED OUT ON BEHALF OF
Zenith Mechanical Services
REPORT NUMBER: 22-21966
DATE OF REPORT: 19/08/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-21966
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Zenith Mechanical Services
Address | Office 82
Viewpoint Business Centre
Consett
DH8 6BN
Site Address | Patton House
Patton Walk
Wheatley Hill
DH6 3QX
Carried Out On | 11/08/2022, 19/08/2022
Survey Completed By | Rob Porritt
SECTION 2: Introduction
Please assess boiler on site @ Patton Walk DH6 3QY. Keysafe 1066 located near fire door.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-21966
SECTION 3: Report
Boiler 2, on arrival to site, boiler 2 is isolated electrically. I completed my visual checks of boiler and flue, all ok, flue integrity pass and no water or gas leaks. I turned on boiler 2 and it did not run, I completed all electrical safety checks and tested boiler components found wiring to lockout indicated snapped and boiler stat disconnected, this can only be manual intervention. I re connected all loose wiring and temporarily linked out lockout indicator, boiler fired. I completed a flue gas analysis of boiler 2 and the results are a FAIL CO ppm 634. On inspection of the heat exchanger and flue hood I recommend a thorough service of boiler 2 As per manufacturers instructions. Combustion to be set correctly at the point of service IF gas valves x 3 are functioning correctly. BOILER 2 IS TURNED OFF. I didn't look too closely at boller 1 ! Boiler 2 returned to site, completed full strip down service of boiler to, replaced ignition and flame electrodes. Completed all safety checks, flue gas analysis, tested boiler on completion of works, all.ok

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-21966
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-21966
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-21966
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-21966
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-21966
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes