## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
3 Park View
Park Road
Lynemouth
NE61 5XL
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 22-23761
DATE OF REPORT: 07/10/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-23761
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | 3 Park View
Park Road
Lynemouth
NE61 5XL
Carried Out On | 06/10/2022, 07/10/2022
Survey Completed By | Rob Porritt
SECTION 2: Introduction
Tenants son has reported that the heating is not working The tenant is 88 and is not able to function properly when he is cold.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-23761
SECTION 3: Report
Tested heating controls, both room stat and w port valve need replacing. Sink unit to be removed or altered to allow access. Materials, 1 x room stat 1 x 22mm honeywell 2 port valve and motor. 2 x 15mm isolation valve 2 x 22mm x 15mm reducers, compression 3m x 15mm copper Em x 22mm copper Isolated and drained flat heating removed and replaced 2 port valve and actuator and fitted new, altered pipework and fitted new isolation val es to w port. Replaced room stat. Connected room stat and 2 port, voltsd fluctuating between 55 volts and 90 volts, 330 volts required, billed out cables supplying room stat and 2 port, found short circuit fault, cable must be nipped or damaged and will need replacing. Operated 2 port valve manually to provide heat to radiators, restricted flow in heating pipework, vented rads and cleared airlock, stilll no flow Removed 2 port valve body and tried to flush pipework, pipework blocked, no flow. FOW, thoroughly flush rads and pipework in flat. Electrician required to run new cables to room stat and and 2 port valve.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-23761
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-23761
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-23761
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-23761
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-23761
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes